BLE Mesh IoT System

MQTT Packet Reference

Unimation | PO-00103 | Rev 1.0 | July 2026

# 1. Overview

This document describes every MQTT packet exchanged between the cloud server and the BLE Mesh gateway, including both commands sent from the cloud to the gateway and acknowledgement packets published by the gateway back to the cloud.

All packets are JSON objects published to or received from the configured MQTT topic. The JsonPacketID field identifies the packet type and is present in every packet.

# 2. Packet ID Reference

## 2.1 Gateway Packets (ID 0–10)

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| 0 | GWY_REG_PACKET | Cloud → Gateway | Register the gateway with the server |
| 1 | GWY_CONF_ACK | Gateway → Cloud | Gateway IR protocol configuration acknowledgement |
| 2 | GWY_UNREG_PACKET | Cloud → Gateway | Unregister the gateway |
| 3 | GWY_AC_CONTROL_PACKET | Cloud → Gateway | Send AC control command to a node |
| 4 | GWY_MANUAL_AC_CONTROL_ACK | Gateway → Cloud | Manual AC control state report from gateway |
| 5 | GWY_RECONF_PACKET | Cloud → Gateway | Reconfigure IR protocol on a node |
| 6 | GWY_HEARTBEAT_ACK | Gateway → Cloud | Periodic gateway status heartbeat |
| 7 | GWY_HEARTBEAT_PUB_CONF_PACKET | Cloud → Gateway | Set heartbeat publish period on gateway |
| 8 | GWY_TEACHING_MODE | Cloud → Gateway / Gateway → Cloud | Enter/exit teaching mode on gateway |
| 9 | GWY_TEACHING_MODE_CMD_SELECTION_PACKET | Cloud → Gateway | Select IR command during teaching mode |
| 10 | GWY_DEBUG_INFO_PACKET | Cloud → Gateway / Gateway → Cloud | Request/report gateway debug info |

## 2.2 Node Packets (ID 100–110)

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| 100 | NODE_PROV_PACKET | Gateway → Cloud | Node provisioned into the mesh network |
| 101 | NODE_CONF_ACK | Gateway → Cloud | Node IR protocol configuration acknowledgement |
| 102 | NODE_UNPROV_PACKET | Cloud → Gateway / Gateway → Cloud | Remove node from mesh network |
| 103 | NODE_AC_CONTROL_PACKET | Cloud → Gateway | Send AC control command to specific node |
| 104 | NODE_MANUAL_AC_CONTROL_ACK | Gateway → Cloud | Manual AC control state report from node |
| 105 | NODE_RECONF_PACKET | Cloud → Gateway | Reconfigure IR protocol on specific node |
| 106 | NODE_HEARTBEAT_ACK | Gateway → Cloud | Periodic node status heartbeat |
| 107 | NODE_HEARTBEAT_PUB_CONF_PACKET | Cloud → Gateway | Set heartbeat publish period on node |
| 108 | NODE_TEACHING_MODE | Cloud → Gateway / Gateway → Cloud | Enter/exit teaching mode on node |
| 109 | NODE_TEACHING_MODE_CMD_SELECTION_PACKET | Cloud → Gateway | Select IR command during node teaching mode |
| 110 | NODE_DEBUG_INFO_PACKET | Cloud → Gateway / Gateway → Cloud | Request/report node debug info |

# 3. Gateway Packet Definitions

## 3.1 GWY_REG_PACKET — Gateway Registration

Sent by the cloud to register the gateway. The gateway stores the Location string in NVS and responds with the registration ACK.

Command (Cloud → Gateway)

{"JsonPacketID": 0, "MsgSeqNo": 1, "Location": "Building A Floor 2"}

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| JsonPacketID | int | 0 | Packet type identifier |
| MsgSeqNo | int | 1–65535 | Message sequence number |
| Location | string | "Building A Floor 2" | Physical location string (max 20 chars) |

Response (Gateway → Cloud)

{"JsonPacketID": 0, "MsgSeqNo": 1, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| JsonPacketID | int | 0 | Packet type identifier |
| MsgSeqNo | int | 1 | Echoed sequence number |
| GwySerNo | string | "GWY00001" | Gateway serial number |
| ErrorCode | int | 1 = SUCCESS | Result code |
| ErrorMsg | string | "SUCCESS" | Human-readable result |

## 3.2 GWY_UNREG_PACKET — Gateway Unregistration

Sent by the cloud to unregister the gateway. Clears registration state from NVS.

Command (Cloud → Gateway)

{"JsonPacketID": 2, "MsgSeqNo": 2}

Response (Gateway → Cloud)

{"JsonPacketID": 2, "MsgSeqNo": 2, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

## 3.3 GWY_CONF_ACK — Gateway IR Protocol Configuration

Published by the gateway to report the currently configured IR protocol.

Packet (Gateway → Cloud)

{"JsonPacketID": 1, "GwySerNo": "GWY00001", "Protocol": "LG2", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| JsonPacketID | int | 1 | Packet type identifier |
| GwySerNo | string | "GWY00001" | Gateway serial number |
| Protocol | string | "LG2" | Configured IR protocol name |
| ErrorCode | int | 1 = SUCCESS | Result code |
| ErrorMsg | string | "SUCCESS" | Human-readable result |

## 3.4 GWY_RECONF_PACKET — Gateway IR Reconfiguration

Sent by the cloud to change the IR protocol on the gateway.

Command (Cloud → Gateway)

{"JsonPacketID": 5, "MsgSeqNo": 3, "Protocol": 14}

Response (Gateway → Cloud)

{"JsonPacketID": 5, "MsgSeqNo": 3, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

## 3.5 GWY_AC_CONTROL_PACKET — AC Control

Sent by the cloud to control the AC unit via the gateway (gateway's own IR blaster, not a node).

Command (Cloud → Gateway)

{"JsonPacketID": 3, "MsgSeqNo": 4, "Power": 1, "Mode": "COOL", "FanSpeed": 2, "Temperature": 24, "SwingH": 0, "SwingV": 0, "OnTimer": 0, "OffTimer": 0, "Locking": 0, "TempLockUpLimit": 0, "TempLockLowLimit": 0}

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| Power | int | 0/1 | 0 = Off, 1 = On |
| Mode | string | "COOL" | AC mode: COOL/HEAT/FAN/DRY/AUTO |
| FanSpeed | int | 0–5 | Fan speed level |
| Temperature | int | 16–30 | Set temperature in °C |
| SwingH | int | 0–5 | Horizontal swing position |
| SwingV | int | 0–5 | Vertical swing position |
| OnTimer | int | 0–1440 | On timer in minutes (0 = disabled) |
| OffTimer | int | 0–1440 | Off timer in minutes (0 = disabled) |
| Locking | int | 0/1 | Temperature locking 0 = off, 1 = on |
| TempLockUpLimit | int | 16–30 | Upper temperature lock limit |
| TempLockLowLimit | int | 16–30 | Lower temperature lock limit |

Response (Gateway → Cloud)

{"JsonPacketID": 3, "MsgSeqNo": 4, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

## 3.6 GWY_HEARTBEAT_ACK — Gateway Heartbeat

Published periodically by the gateway at the configured publish period. Contains the last known AC state plus ambient temperature readings from the gateway's sensors.

Packet (Gateway → Cloud)

{"JsonPacketID": 6, "GwySerNo": "GWY00001", "Power": 1, "Mode": "COOL", "FanSpeed": 2, "Temperature": 24, "AmbientTemperature(Digital)": 27, "AmbientTemperature(Analog)": 26, "SwingH": 0, "SwingV": 0, "OnTimer": 0, "OffTimer": 0, "Locking": 0, "TempLockUpLimit": 0, "TempLockLowLimit": 0}

## 3.7 GWY_HEARTBEAT_PUB_CONF_PACKET — Set Heartbeat Period

Sent by the cloud to change the heartbeat publish period on the gateway.

Command (Cloud → Gateway)

{"JsonPacketID": 7, "MsgSeqNo": 5, "PublishPeriodSec": 60}

Response (Gateway → Cloud)

{"JsonPacketID": 7, "MsgSeqNo": 5, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

## 3.8 GWY_TEACHING_MODE — Gateway Teaching Mode

Initiates IR teaching mode on the gateway. The gateway records raw IR signals from an existing remote for each temperature step.

Command (Cloud → Gateway)

{"JsonPacketID": 8, "MsgSeqNo": 6, "TeachingStart": 1, "StartingTemperature": 18, "EndingTemperature": 30, "ErrorCheckEnabled": 1}

Response (Gateway → Cloud)

{"JsonPacketID": 8, "MsgSeqNo": 6, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "ENTERED_TEACHING_MODE", "RemainingCommands": 13, "LastCommand": "NONE"}

## 3.9 GWY_TEACHING_MODE_CMD_SELECTION_PACKET — Select Teaching Command

Sent during teaching mode to advance to the next IR command recording step.

Command (Cloud → Gateway)

{"JsonPacketID": 9, "MsgSeqNo": 7}

Response (Gateway → Cloud)

{"JsonPacketID": 9, "MsgSeqNo": 7, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

## 3.10 GWY_DEBUG_INFO_PACKET — Gateway Debug Info

Sent by the cloud to request gateway diagnostics. The gateway responds with firmware version, uptime, registration state, and configuration.

Command (Cloud → Gateway)

{"JsonPacketID": 10, "MsgSeqNo": 8}

Response (Gateway → Cloud)

{"JsonPacketID": 10, "MsgSeqNo": 8, "GwySerNo": "GWY00001", "ErrorCode": 1, "ErrorMsg": "SUCCESS", "FirmwareVersion": "1.0.4", "Registered": 1, "Protocol": "LG2", "PublishPeriodSec": 300, "DeviceUpTimeHrs": "2.50"}

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| FirmwareVersion | string | "1.0.4" | Major.Minor.Patch version |
| Registered | int | 0/1 | 1 = registered with server |
| Protocol | string | "LG2" | Active IR protocol |
| PublishPeriodSec | int | 60–3600 | Current heartbeat period in seconds |
| DeviceUpTimeHrs | string | "2.50" | Device uptime in hours |

## 3.11 GWY_MANUAL_AC_CONTROL_ACK — Manual AC Control Report

Published by the gateway when it detects a manual AC state change (e.g. user pressed remote). Reports the decoded AC state.

Packet (Gateway → Cloud)

{"JsonPacketID": 4, "GwySerNo": "GWY00001", "Power": 1, "DetectedTemperature": 24, "Temperature": 24, "FanSpeed": 2, "Mode": "COOL", "PowerErrorCode": 0, "TemperatureErrorCode": 0, "FanSpeed": 0, "ModeErrorCode": 0}

# 4. Node Packet Definitions

## 4.1 NODE_PROV_PACKET — Node Provisioned

Published by the gateway when a new BLE Mesh node is successfully provisioned and joins the network. No command — event-driven.

Packet (Gateway → Cloud)

{"JsonPacketID": 100, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| JsonPacketID | int | 100 | Packet type identifier |
| GwySerNo | string | "GWY00001" | Gateway serial number |
| NodeSerNo | string | "NODE00042" | Newly provisioned node serial number |
| ElementAddr | int | 5 | BLE Mesh unicast address assigned to the node |
| ErrorCode | int | 1 = SUCCESS | Provisioning result code |
| ErrorMsg | string | "SUCCESS" | Human-readable result |

## 4.2 NODE_CONF_ACK — Node IR Protocol Configuration

Published by the gateway to report the IR protocol configured on a specific node.

Packet (Gateway → Cloud)

{"JsonPacketID": 101, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "Protocol": "LG2", "ErrorCode": 1, "ErrorMsg": "SUCCESS"}

## 4.3 NODE_UNPROV_PACKET — Node Unprovisioned

Sent by the cloud to remove a node from the mesh. The node removes itself and the gateway deletes it from its database. Also published by the gateway as an event when deprovision completes.

Command (Cloud → Gateway)

{"JsonPacketID": 102, "MsgSeqNo": 10, "ElementAddr": 5}

Response (Gateway → Cloud)

{"JsonPacketID": 102, "MsgSeqNo": 10, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "SUCCESS", "BleErrorCode": 0}

## 4.4 NODE_AC_CONTROL_PACKET — Node AC Control

Sent by the cloud to control the AC unit connected to a specific node via its IR blaster.

Command (Cloud → Gateway → Node)

{"JsonPacketID": 103, "MsgSeqNo": 11, "ElementAddr": 5, "Power": 1, "Mode": "COOL", "FanSpeed": 2, "Temperature": 24, "SwingH": 0, "SwingV": 0, "OnTimer": 0, "OffTimer": 0, "Locking": 0, "TempLockUpLimit": 0, "TempLockLowLimit": 0}

Response (Node → Gateway → Cloud)

{"JsonPacketID": 103, "MsgSeqNo": 11, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "SUCCESS", "BleErrorCode": 0, "RSSI_dBm": -65}

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| BleErrorCode | int | 0 = ESP_OK | BLE Mesh transmission error code from ESP-IDF |
| RSSI_dBm | int | -65 | BLE signal strength of last received message from this node (dBm) |

## 4.5 NODE_RECONF_PACKET — Node IR Reconfiguration

Sent by the cloud to change the IR protocol on a specific node.

Command (Cloud → Gateway → Node)

{"JsonPacketID": 105, "MsgSeqNo": 12, "ElementAddr": 5, "Protocol": 14}

Response (Node → Gateway → Cloud)

{"JsonPacketID": 105, "MsgSeqNo": 12, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "SUCCESS", "BleErrorCode": 0}

## 4.6 NODE_HEARTBEAT_ACK — Node Heartbeat

Published periodically by each node at its configured publish period. Contains the node's current AC state and ambient temperature readings.

Packet (Node → Gateway → Cloud)

{"JsonPacketID": 106, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "Power": 1, "Mode": "COOL", "FanSpeed": 2, "Temperature": 24, "AmbientTemperature(Digital)": 27, "AmbientTemperature(Analog)": 26, "SwingH": 0, "SwingV": 0, "OnTimer": 0, "OffTimer": 0, "Locking": 0, "TempLockUpLimit": 0, "TempLockLowLimit": 0}

## 4.7 NODE_HEARTBEAT_PUB_CONF_PACKET — Set Node Heartbeat Period

Sent by the cloud to change the heartbeat publish period on a specific node.

Command (Cloud → Gateway → Node)

{"JsonPacketID": 107, "MsgSeqNo": 13, "ElementAddr": 5, "PublishPeriodSec": 60}

Response (Node → Gateway → Cloud)

{"JsonPacketID": 107, "MsgSeqNo": 13, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "SUCCESS", "BleErrorCode": 0}

## 4.8 NODE_TEACHING_MODE — Node Teaching Mode

Initiates IR teaching mode on a specific node. The node records raw IR signals step by step for each temperature.

Command (Cloud → Gateway → Node)

{"JsonPacketID": 108, "MsgSeqNo": 14, "ElementAddr": 5, "TeachingStart": 1, "StartingTemperature": 18, "EndingTemperature": 30, "ErrorCheckEnabled": 1}

Response (Node → Gateway → Cloud)

{"JsonPacketID": 108, "MsgSeqNo": 14, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "ENTERED_TEACHING_MODE", "BleErrorCode": 0, "RemainingCommands": 13, "LastCommand": "NONE"}

## 4.9 NODE_TEACHING_MODE_CMD_SELECTION_PACKET — Select Node Teaching Command

Command (Cloud → Gateway → Node)

{"JsonPacketID": 109, "MsgSeqNo": 15, "ElementAddr": 5}

Response (Node → Gateway → Cloud)

{"JsonPacketID": 109, "MsgSeqNo": 15, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "SUCCESS", "BleErrorCode": 0}

## 4.10 NODE_DEBUG_INFO_PACKET — Node Debug Info

Sent by the cloud to request diagnostics from a specific node. On success, the gateway relays the node's firmware version, uptime, and configuration.

Command (Cloud → Gateway → Node)

{"JsonPacketID": 110, "MsgSeqNo": 16, "ElementAddr": 5, "RestartDevice": 0, "ResetDevice": 0}

Response (Node → Gateway → Cloud)

{"JsonPacketID": 110, "MsgSeqNo": 16, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "ErrorCode": 1, "ErrorMsg": "SUCCESS", "BleErrorCode": 0, "FirmwareVersion": "1.0.3", "Protocol": "LG2", "PublishPeriodSec": 300, "DeviceUpTimeHrs": "1.25"}

## 4.11 NODE_MANUAL_AC_CONTROL_ACK — Node Manual AC Control Report

Published by the gateway when a node detects a manual AC state change via its IR receiver.

Packet (Node → Gateway → Cloud)

{"JsonPacketID": 104, "GwySerNo": "GWY00001", "NodeSerNo": "NODE00042", "ElementAddr": 5, "Power": 1, "DetectedTemperature": 24, "FanSpeed": 2, "Mode": "COOL", "PowerErrorCode": 0, "TemperatureErrorCode": 0, "FanSpeed": 0, "ModeErrorCode": 0}

# 5. Common Fields

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| JsonPacketID | int | 0–110 | Identifies the packet type. Present in every packet. |
| MsgSeqNo | int | 1–65535 | Sequence number. Echoed in response. Present in commands and responses. |
| GwySerNo | string | "GWY00001" | Gateway serial number. Present in all packets published by gateway. |
| NodeSerNo | string | "NODE00042" | Node serial number. Present in all node packets. |
| ElementAddr | int | 3–65534 | BLE Mesh unicast address of the target/source node. |
| ErrorCode | int | 1 = SUCCESS | Operation result. See Section 6 for all codes. |
| ErrorMsg | string | "SUCCESS" | Human-readable error code name. |
| BleErrorCode | int | 0 = ESP_OK | ESP-IDF BLE stack error code. 0 = no error. |
| RSSI_dBm | int | -65 | BLE signal strength of the node's last message at the gateway receiver (dBm). Negative value; closer to 0 is stronger. |

# 6. Error Code Values

The following error codes can appear in the ErrorCode field. ErrorMsg contains the string name.

| Field | Type | Value / Example | Description |
| --- | --- | --- | --- |
| -1 | FAILURE | — | Generic failure |
| 0 | SUCCESS | — | Operation succeeded (note: enum starts at 0 after FAILURE=-1) |
| 1 | JSON_PACKET_INVALID | — | Received JSON is malformed |
| 2 | MISSING_PACKET_ID | — | JsonPacketID field missing |
| 3 | PACKET_ID_EXCEEDING_RANGE | — | JsonPacketID out of valid range |
| 4 | MISSING_MSG_SEQ_NO | — | MsgSeqNo field missing |
| 8 | NODE_COMM_TIMEOUT | — | No response received from node over BLE Mesh |
| 9 | GWY_NOT_REG | — | Gateway is not registered — register first |
| 10 | GWY_ALREADY_REG | — | Gateway is already registered |
| ... | ... | — | See lte.h error_codes enum for full list |

# 7. Notes

• All packets are published to the configured MQTT topic as UTF-8 encoded JSON strings.

• Commands from cloud arrive on the subscribe topic; gateway responses are published to the publish topic.

• The gateway queues commands for nodes internally. If a node does not respond within the timeout period, ErrorCode NODE_COMM_TIMEOUT is returned.

• BleErrorCode is the raw ESP-IDF error code from the BLE Mesh stack. 0 (ESP_OK) means the BLE transmission succeeded. Non-zero values indicate a BLE layer failure independent of the Modbus/application result.

• RSSI_dBm is only present in packets that originate from a node (not gateway-only packets). Typical range is -40 dBm (strong) to -90 dBm (weak).

• All node packets are forwarded through the gateway. The cloud never communicates directly with nodes.