Inspironics – Amenos

Hub communication packet Document (V0.9)

25 August 2020

25 August 2020

Revision History

| Doc Version | Release Date | Prepared by | Remarks |
| --- | --- | --- | --- |
| 0.1 | 27 April 2020 | Hari Prasath A | Initial Version |
| 0.2 | 2 May 2020 | Hari Prasath A | Added KINISI communication packet and initiate ZigBee device (light) pair packet |
| 0.3 | 14 May 2020 | Hari Prasath A | Added room and AC temperature value in Amenos sensor packet |
| 0.4 | 29 May 2020 | Hari Prasath A | Updated customer review commands given on 15 May 2020 |
| 0.5 | 01 June 2020 | Hari Prasath A | Added ZigBee device(light) health status and Decommission packet added |
| 0.6 | 25 June 2020 | Hari Prasath A | Added OTAP, section 3.1, 3.11,3.12 and updated 3.3 |
| 0.7 | 16 July 2020 | Hari Prasath A | Updated section 2.5.1, 2.5.2 ,2.2 added section 3.13, 3.14,3.15,3.16, 2.5, 3.10 |
| 0.8 | 10 August 2020 | Hari Prasath A | Added 2.5, 3.8,3.18 and updated section 2,3 |
| 0.9 | 25 August 2020 | Hari Prasath A | Added 3.14,2.8.2,updated 2.1 |

Ref. no.: QM/IIL/AMENOS-HUB-COMM/August 25

- Table of Contents

1	Document Purpose	6

2	Sensor to Hub	6

2.1	Device registration packets	6

2.1.1	Amenos registration packet	6

2.1.2	Kinisi registration packet	6

2.1.3	Light registration packet	7

2.2	Device health status	7

2.2.1	Amenos health status	7

2.2.2	Kinisi health status	7

2.2.3	Light health status	8

2.3	Sensor data	8

2.3.1	Amenos sensor data	8

2.3.2	Kinisi event data	9

2.4	Light Registration ACK packet	9

2.5	AC fail packet	10

2.6	Maintenance ACK	10

2.7	Firmware update ACK	10

2.8	Amenos event data	10

2.8.1	AC event  packet	11

2.8.2	Light event packet	11

3	Hub to sensor	11

3.1	Maintenance ON/OFF packet	11

3.2	Firmware update command	12

3.3	Mobile IP Address information	12

3.4	Enable Ble mesh packet	12

3.5	Shutdown & control packet	13

3.5.1	Sensor shutdown packet	13

3.5.2	AC control packet	13

3.5.3	Zone light control packet	14

3.6	Device registration ACK packet	14

3.6.1	Amenos ACK packet	14

3.6.2	Kinisi ACK packet	14

3.7	Decommission packet	15

3.7.1	Amenos Decommission packet	15

3.7.2	Kinisi Decommission packet	15

3.7.3	Light Decommission packet	15

3.8	Registration request packet	16

3.9	AC  & Light default setting packet	16

3.9.1	Amenos AC default packet	16

3.9.2	Amenos Light default packet	17

3.10	Light configuration packet	18

3.11	Lock capacitive touch switch packet	19

3.12	Force set temperature packet	19

3.13	Amenity Sleep mode setting packet	19

3.14	Over temperature wake after packet	20

3.15	AC  & Light default broadcast packet	20

3.15.1	Amenos AC default broadcast packet	20

3.15.2	Amenos Light default broadcast packet	21

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Acronyms and Abbreviations

| AC | Air Conditioner |
| --- | --- |
| ACK | Positive Acknowledgement |
| UDP | User Datagram Protocol |

# Document Purpose

The purpose of this document is to describe communication packet between Hub and Amenos over Wi-Fi interface using UDP protocol

# Sensor to Hub

# Hereafter Amenos is being referred to as Sensor. For more details on field value refer Data Dictionary.

## Device registration packets

This packet is sent to register the sensor to Hub. After sending this packet to Hub, sensor wait for ACK from Hub.

### Amenos registration packet

{

“hmac”:””,

“payload”:{

"device_uid":"031219010010002",

"data_type":1,

"device_data":[

{

"device_type":5,

“auth_code”:”3A2B1C45673E”,

"product_model":"AMENOS1",

"firmware_version":"1.0",

"mfg_date":"10-12-2000",

"device_operational_mode":1,

"device_variant":”0x0010”,

"org_uid":"012",

"faciliti_uid":"K12",

"amenity_name":"SPA001",

"device_name":"1001AAIR01",

"timestamp":"2019 -12 -24T05:15:09Z ",

}

]

}

}

### Kinisi registration packet

{

“hmac”:””,

“payload”:{

"device_uid":"031219010010005",

"data_type":1,

"device_data":[

{

"device_type":6,

“auth_code”:”3A2B1C45673E”,

"product_model":"KINISI01",

"firmware_version":"1.0",

"mfg_date":"10-12-2000",

"device_operational_mode":3,

"device_variant":”0x6000”,

"org_uid":"012",

"faciliti_uid":"K12",

"amenity_name":"SPA001",

"device_name":"KINI1",

"timestamp":"2019 -12 -24T05:15:09Z "

}

]

}

}

### Light registration packet

This packet is sent to Hub to register the newly connected light device with sensor

{

“hmac”:””,

“payload”:{

"device_uid":"23E7843D383B4A32",

"data_type":1,

"device_data":[

{

"device_type":8,

"mfg_date":"10-12-2000",

"device_operational_mode":3,

"org_uid":"012",

"faciliti_uid":"K12",

"amenity_name":"SPA001",

"device_name":"1001AAIR01",

“zone”:1/2/3,

"timestamp":"2019 -12 -24T05:15:09Z ",

} ]

}

}

## Device health status

This packet act as “Heartbeat” to know that sensor is alive. Sensor should send this packet at 1 sec interval

### Amenos health status

{

“hmac”:””,

“payload”: {

"device_uid":"031219010010002",

"data_type":2,

"device_data”: [

{

"device_health_status":0,

"device_temperature":+25/-10,

}

]

}

}

device_temperature can be both positive and negative. Sign is given for identification

### Kinisi health status

{

“hmac”:””,

“payload”:{

"device_uid":"031219010010005",

"data_type":2,

"device_data":[

{

"device_health_status":0,

"device_temperature":0,

}

]

}

}

### Light health status

{

“hmac”:””,

“payload”:{

"device_uid":"23E7843D383B4A32",

"data_type":2,

"device_data":[

{

"device_health_status":0,

"device_temperature":0,

"device_health_status":1

}

]

}

}

(Note :

“Night Lamps”  	- 1

“Living Space” 	- 2

“Corridor“       - 3

)

## Sensor data

This packet is used to send sensor data (temperature, light intensity, battery voltage) to Hub. Sensor should send this packet at 1 min interval or whenever user sets the AC temperature.

### Amenos sensor data

{

“hmac”:””,

“payload”:{

"device_uid":"031219010010002",

"data_type":3,

"device_data":[

{

"sender_uid":"Amenos",

"packet_type":3,

"room_temperature":+34/-10,

"set_ac_temperature":20,

“relay1_count”:56,

“relay2_count”:56,

“relay3_count”:56,

}

]

}

}

(NOTE:

"ac_status"   :	1 – AC ON

0 – AC OFF

"mode"	   :	"001"  - Cool

"010" - Auto

"100" - Dry

"101" – Fan

"light_status":	1 – Turn ON light

0 – Turn OFF light

For Split AC relay count will send as 0

device_temperature can be both positive and negative. Sign is given for identifcation

)

### Kinisi event data

This packet is used to send movement detection to Hub. This packet is sent whenever there is any movement detected in Kinisi. This is event-based packet.

{

“hmac”:””,

“payload”:{

"device_uid":"031219010010005",

"data_type":3,

"device_data":[

{

"sender_uid":"Kinisi",

"packet_type":3,

“battery_percentage”:50,

“occupancy_detection”:1

}

]

}

## Light Registration ACK packet

Sensor send this packet to Hub to indicate light registration status in Amenos. “address_id” is same as light mac id all over the document

{

“hmac”:’’,

“payload”:

{

“device_uid” : “031219010010002”,

"data_type":4,

“device_data”:[

{

"address_id":"23E7843D383B4A32",

“ack_type”:1,

“status”:1

}

]

}

}

(NOTE:  “status” indicates the registration status of light device

“ack_type”:1 – Light device registered successfully

“ack_type”:0 – Light device registration failed)

## AC fail packet

Sensor send this packet to Indicate that room temperature has not fallen despite AC being turned ON.

{

“hmac”:’’”,

“payload”:

{

"device_uid":"031219010010002",

"data_type":5,

"device_data":[

{

"alert_type": 10,

"time_ac_run": 60,

"ac_set_temperature": 23,

"room_temperature": 23,

}

]

}

}

## Maintenance ACK

Sensor send this acknowledgement packet when it receives Maintenance ON/OFF packet

{

“hmac”:’’”,

“payload”:

{

"device_uid":"031219010010002",

"data_type":6,

"device_data":[

{

"ack": 1,

}

]

}

}

## Firmware update ACK

Sensor send this packet to update the OTAP status

{

“hmac”:’’”,

“payload”:

{

"device_uid":"031219010010002",

"data_type":7,

"device_data":[

{

"ack": 1,

}

]

}

}

## Amenos event data

## AC event  packet

## Sensor send this packet to update AC status at every POR. This packet will be sent whenever there is status change or any field are updated via PORTA. This is event-based packet

{

“hmac”:’’”,

“payload”:

{

"device_uid":"031219010010002",

"data_type":8,

"device_data":[

{

"action_type": 3,

"ac_status": 1,

“mode” : “auto”,

“set_ac_temperature”:23,

"time_ac_run": 60,

}

]

}

}

### Light event packet

This packet is used to send light data like status, brightness, color to Hub. This packet is sent whenever there is status change on the bulbs. This is event based packet.

{

“hmac”:’’”,

“payload”:

{

"device_uid":"031219010010002",

"data_type":8,

"device_data":[

{

"action_type": 4,

"zone": 1,

"total_on_time": 300,

"bulb_status": 1,

}

]

}

}

# Hub to sensor

## Maintenance ON/OFF packet

Sensor receives this packet to turn ON/OFF maintenance mode

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 6,

“device_data”:[

{

“maintenance_mode”: 1/0

}

]

}

}

(NOTE:  “maintenance_mode” indicates the state of maintenance

“maintenance_mode”:1 – Turn ON maintenance

“maintenance_mode”:0 – Turn OFF maintenance)

## Firmware update command

Hub will send this packet to enable firmware update process in devices using ftp.

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 7,

“device_data”:[

{

“firmware_version”: “1.0.1”,

"firmware_path": "ftp://<HUB_IP>/Amenos",

"crc": " " ,

"file_size" : "10"

}

]

}

}

## Mobile IP Address information

### Sensor receives this packet to transfer log data to mobile

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 8,

“device_data”:[

{

“ipaddr”: “02345d4f5”

}

]

}

}

## Enable Ble mesh packet

Sensor receive this packet to enable BLE mesh

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 9,

“device_data”:[

{

“enable_mesh”: 1;

}

]

}

}

## Shutdown & control packet

## Sensor shutdown packet

Hub will send this packet to Switch ON/OFF the power supply to Sensors. Hub will multicast devices  should save configuration and go to minimum power mode.

{

“hmac”:””,

“payload”:{

“device_uid” : HUB1 ,

“action”:10,

“device_data”:[

{

"command_type": 1,

“amenity-name”: “Room-101”,

“turn_off_power”:1/0

}

]

}

}

### AC control packet

Sensor receives this packet to control the Split AC.

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 10,

“device_data”:[

{

"command_type": 3,

"ac_status":1/0,

"mode":"001"/"010"/"100"/"101",

"ac_temperature":16-28,

}

]

}

}

(NOTE:

"ac_status":	1 – AC ON

0 – AC OFF

"mode":		"001"  - Cool

"010" - Auto

"100" - Dry

"101" - Fan

"temperature":16-28

For HVAC Dry & Fan mode is not supported)

### Zone light control packet

Sensor receives this packet to control the registered zone light device

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 10,

“device_data”:[

{

"command_type": 4,

“zone”: 1/2/3

“color”:<rrggbb>,

"light_status":1/0,

"brightness":15,

}

]

}

}

(NOTE: "light_status":1 – Turn ON light

"light_status":0 – Turn OFF light

“Night Lamps”  	- 1

“Living Space” 	- 2

“Corridor“       - 3

)

## Device registration ACK packet

Sensor receive this ACK packet from Hub to know that sensor is registered or not, after sending Device registration packet

### Amenos ACK packet

{

“hmac”:’’,

“payload”:

{

“device_uid” : “031219010010002”,

“action”:11,

“device_data”:[

{

“ack_type”:1,

“status”:1/0

}

]

}

}

### Kinisi ACK packet

{

“hmac”:’’,

“payload”:

{

“device_uid” : “031219010010005”,

“action”:11,

“device_data”:[

{

“ack_type”:1,

“status”:1/0

}

]

}

}

(NOTE:  “ack_type ” indicates the registration status of sensor

“status ”:1 – Device registered successfully

## “status ”:0 – Device registration failed)

## Decommission packet

After receiving this packet sensor should operate in Configuration mode

### Amenos Decommission packet

{

“hmac”:’’,

“payload”:{

“device_uid”:”031219010010002”

“action”:12,

“device_data”:[

{

}

]

}

}

### Kinisi Decommission packet

{

“hmac”:’’,

“payload”:{

“device_uid”:”031219010010002”

“action”:12,

“device_data”:[

{

“Kinisi_uid”:”031219010010008”

}

]

}

}

### Light Decommission packet

{

“hmac”:’’,

“payload”:{

“device_uid”:”031219010010002”

“action”:12,

“device_data”:[

{

"address_id":"23E7843D383B4A32"

}

]

}

## }

## Registration request packet

Hub will send this packet if it is rebooted accidentally

{

“hmac”:’’,

“payload”:

{

“device_uid” : “031219010010002”,

“action”:14,

“device_data”:[

{

“reg_required”:1

}

]

}

}

## AC  & Light default setting packet

Sensor receives this packet after it successfully registered with Hub

### Amenos AC default packet

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 15,

“device_data”:[

{

"default_type": 1,

"schedule": [

{

"from_time": "00:0000",

"to_time": "12:59:59",

"ac_status": 1,

"mode": "001",

"temperature": 26

},

{

"from_time": "13:00:00",

"to_time": "19:59:59",

"ac_status": 1,

"mode": "101",

"temperature": 18

},

{

"from_time": "20:00:00",

"to_time": "23:59:59",

"ac_status": 1,

"mode": "100",

"temperature": 28

}

]

}

]

}

}

(NOTE:

"ac_status":	1 – AC ON

0 – AC OFF

"mode":		"001"  - Cool

"010" - Auto

"100" - Dry

"101" - Fan

"temperature":16-28

HVAC mode does not support Dry & Fan AC Mode

)

### Amenos Light default packet

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 15,

“device_data”:[

{

"default_type": 2,

"schedule": [

{

"from_time": "00:00:00",

"to_time": "12:59:59",

"zone_settings": [

{

"zone": 1,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 15,

"temperature": 1500

},

{

"zone": 2,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 20,

"temperature": 1500

},

{

"zone": 3,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 20

"temperature": 1500

}

]

},

{

"from_time": "13:00:00",

"to_time": "23:59:59",

"zone_settings": [

{

"zone": 1,

"color": "0xFFFF00",

"light_status": 0,

"brightness": 35,

"temperature": 1500

},

{

"zone": 2,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 40,

"temperature": 1500

},

{

"zone": 3,

"color": "0xFFFF00",

"light_status": 0,

"brightness": 50,

"temperature": 1500

}

]

}

]

}

]

}

}

## light_macid is same as light_epid all over the document

## Light configuration packet

Sensor will receive this packet when any new light need to be configured under Amenos

{

“hmac”:’’,

“payload”:

{

“device_uid” : “031219010010002”,

“action”:16,

“device_data”:[

{

“zone” : 1/2/3,

"address_id": "23E7843D383B4A32",

"mfg_date": “2019-06-25”,

"org_uid": "IIL",

"facility_uid": "IIH",

"device_name": "1001ASMB01",

"amenity_name": "1001A"

}

]

}

}

(NOTE:

“Night Lamps”  	- 1

“Living Space” 	- 2

“Corridor“       - 3

)

## Maintenance ON/OFF packet

Sensor receives this packet to turn ON/OFF maintenance mode

### Amenos maintenance ON/OFF packet

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 6,

“device_data”:[

{

“maintenance_mode”: 1/0

}

]

}

}

(NOTE:  “maintenance_mode” indicates the state of maintenance

“maintenance_mode”:1 – Turn ON maintenance

“maintenance_mode”:0 – Turn OFF maintenance)

## Lock capacitive touch switch packet

Sensor receives this packet to enable / disable the touch button press

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 17,

“device_data”:[

{

“status”:1/0

}

]

}

}

(Note: 1 – Don’t consider touch button press

0 – consider touch button press)

## Force set temperature packet

Sensor receives this packet when user wants to lock the button press for setting temperature by forcedly setting to desired temperature

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 18,

“device_data”:[

{

“status” : 1/0,

"ac_status":1/0,

"temperature":16-28

}

]

}

}

(Note:

“status”: 1 – Enable this setting

“status”: 0 – Disable this setting

"ac_status":1 – Turn ON AC

"ac_status":0 – Turn OFF AC)

## Amenity Sleep mode setting packet

Sensor receives this packet when user is going to sleep (i.e. user press sleep mode switch in AFI). When it receives, it will turn off all light and set AC in sleep mode setting.

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 19,

“device_data”:[

{

“status”:1/0

}

]

}

}

(Note: 1 – Enable sleep mode setting

0 – Disable sleep mode setting)

## Over temperature wake after packet

Sensor receives this packet when Hub detects sensor’s device temperature is greater than over temperature

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 20

“device_data”:[

{

“status”:1

}

]

}

}

## AC  & Light default broadcast packet

Sensor receives this packet if the defaults changes

### Amenos AC default broadcast packet

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 21,

“device_data”:[

{

"default_type": 1,

"schedule": [

{

"from_time": "00:0000",

"to_time": "12:59:59",

"ac_status": 1,

"mode": "001",

"temperature": 26

},

{

"from_time": "13:00:00",

"to_time": "19:59:59",

"ac_status": 1,

"mode": "101",

"temperature": 18

},

{

"from_time": "20:00:00",

"to_time": "23:59:59",

"ac_status": 1,

"mode": "100",

"temperature": 28

}

]

}

]

}

}

(NOTE:

"ac_status":	1 – AC ON

0 – AC OFF

"mode":		"001"  - Cool

"010" - Auto

"100" - Dry

"101" - Fan

"temperature":16-28

HVAC mode does not support Dry & Fan AC Mode

)

### Amenos Light default broadcast packet

{

“hmac”:’’,

“payload”:

{

“device_uid”: “031219010010002”,

“action”: 15,

“device_data”:[

{

"default_type": 2,

"schedule": [

{

"from_time": "00:00:00",

"to_time": "12:59:59",

"zone_settings": [

{

"zone": 1,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 15,

"temperature": 1500

},

{

"zone": 2,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 20,

"temperature": 1500

},

{

"zone": 3,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 20

"temperature": 1500

}

]

},

{

"from_time": "13:00:00",

"to_time": "23:59:59",

"zone_settings": [

{

"zone": 1,

"color": "0xFFFF00",

"light_status": 0,

"brightness": 35,

"temperature": 1500

},

{

"zone": 2,

"color": "0xFFFF00",

"light_status": 1,

"brightness": 40,

"temperature": 1500

},

{

"zone": 3,

"color": "0xFFFF00",

"light_status": 0,

"brightness": 50,

"temperature": 1500

}

]

}

]

}

]

}

}

~~~~~~~~~~~~~~~~~~~~~~~~~~End of Document~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~~